SIS life-cycle: Overview of typical activities and documents

This document provides an overview of typical Functional Safety activities and documents based on IEC 61511:2017. The overview can be used to manage Functional Safety projects.

| - Set up functional safety management plan |  | status |
| --- | --- | --- |
| Responsible | Project/plant manager | 🗸 |
| Objective | To manage the development, realisation and maintenance of a SIS | 🗸 |
| Basis | Project definition, basis for design, Process Flow Schemes, P&IDs | 🗴 |
| Activities: Personnel | Determine which departments / personnel need to be involved during the relevant SIS lifecycle phases |  |
|  | Determine competence requirements for the key personnel |  |
|  | Check competence of key personnel |  |
| Planning | Determine the applicable SIS life-cycle phases and the relevant activities and documents (this overview may help) |  |
|  | Make a realistic planning when activities should be performed |  |
| Development process | A verification system should be set up in order to guarantee the quality of activities and documents All documents shall be checked and approved |  |
| Deliverables | Functional safety management plan |  |
|  | Life-cycle planning |  |
| Reference: IEC 61511 clauses 5, 6 and 7 |  |  |

| - Hazard and risk assessment |  | status |
| --- | --- | --- |
| Responsible | Process safety engineer / Process engineer |  |
| Objective | To identify all process hazards and to determine associated risks |  |
| Basis | P&IDs and other relevant conceptual documents |  |
| Activities | Determine scope of work |  |
|  | Organise HAZOP and risk assessment brainstorm sessions |  |
|  | Determine team composition for the brainstorm sessions |  |
|  | Check if the proposed HAZOP chairman is well-experienced |  |
|  | Ensure that appropriate HAZOP and risk assessment methodologies will be used |  |
| Deliverable | HAZOP and Risk Assessment report |  |
| Reference: IEC 61511 clause 8 |  |  |

| - Allocation of safety functions to protection layers |  | status |
| --- | --- | --- |
| Responsible | Process engineer / Process safety engineer |  |
| Objective | To select appropriate risk reducing measures |  |
| Basis | HAZOP and Risk Assessment report and P&IDs |  |
| Activities | Inherently safe design is preferred Mechanical safeguards may be selected as well as instrumental safeguards or other means of risk reduction Determine the instrumental safeguards (SIFs) and associated SIL |  |
| Deliverable | Allocation report (might be an addendum of the HAZOP+RA report) |  |
| Reference: IEC 61511 clause 9 |  |  |

| - Safety Requirements Specifications (SRS) |  | status |
| --- | --- | --- |
| Responsible | Process safety engineer |  |
| Objective | To specify the SIFs to be able to design these SIFs. |  |
| Basis | Allocation report, HAZOP and risk assessment report, P&IDs |  |
| Activities | Define all SIFs; sensors, logic solver function, final elements, overrides (if any), reset functions, Process Safety Times, if valves should be tight shut-off, required risk reduction factor (or PFD) |  |
|  | A SRS is a multidisciplinary document. It must be approved by the involved disciplines |  |
|  | Make Cause & Effect diagrams to be used by the FLD designers, during verification / validation and Operations |  |
| Deliverables | Detailed SRSs |  |
|  | Cause & Effects diagram(s) |  |
| Reference: IEC 61511 clause 10 |  |  |

| - Functional Safety Assessment stage 1 (FSA 1) |  | status |  |
| --- | --- | --- | --- |
| Responsible | Independent competent engineer |  |  |
| Objective | To ensure that the SIS life-cycle activities up to and including the SRS have been performed correctly Note: The SRS is a critical document, it will be used for the design of the SIFs and it will be used as basis for the verification / validation |  |  |
| Basis | SRSs, P&IDs, HAZOP and risk assessment report, allocation report |  |  |
| Activities | Verification if involved personnel are competent |  |  |
|  | Verification if the SRSs are correct and complete |  |  |
|  | Verification if the Cause & Effects diagrams are correct |  |  |
| Deliverable | FSA 1 report |  |  |
| Reference: IEC 61511 clause 5.2.6.1 |  |  |  |

| - Design of the SIS |  | status |
| --- | --- | --- |
| Responsible | Instrumentation engineer |  |
| Objective | To develop the detailed design of the SIS |  |
| Basis | SRS and P&IDs |  |
|  | Narratives, company / project terms of reference, FSA-1 report |  |
| Activities | Specify all instruments, systems and auxiliaries to be purchased |  |
|  | Design the wiring / cabling, power supply, instr. air provisions, etc. |  |
|  | Design the human-machine interfaces |  |
|  | Develop the Application Program |  |
|  | Perform a SIS security risk assessment |  |
|  | Perform audits |  |
|  | Verify if the SIF design comply with IEC 61511 / 61508 |  |
| Typical design deliverables | Specification / requisition of the SIS logic solver |  |
|  | SIS Instruments data sheets |  |
|  | Specification / requisition of the SIS instruments |  |
|  | SIS auxiliary cabinets configuration |  |
|  | Specification / requisition of the SIS auxiliary cabinets |  |
|  | Specification / requisitions of SIS valves / actuators / solenoid valves |  |
|  | SIS Functional Logic Diagrams |  |
|  | SIS Application Program |  |
|  | SIS Application Program verification report |  |
|  | Human-machine interfaces for Operations and Maintenance |  |
|  | Wiring diagrams |  |
|  | Lay out drawings |  |
|  | SIS Loop diagrams |  |
|  | Supporting provisions, tracing and insulation |  |
| Typical other deliverables | SIS security risk assessment report |  |
|  | SIL design verification report |  |
|  | Vendors audit reports. Reviews to be performed to ensure that the vendors functional safety management systems are in place |  |
|  | SIFs test procedures |  |
|  | Loop test procedures |  |
|  | FAT procedures |  |
|  | SIS maintenance management database |  |
|  | SIS installation plan |  |
|  | SIS validation procedures |  |
|  | Evaluation forms of suppliers quotations / documents / safety manuals |  |
|  | Spare parts list |  |
| Reference: IEC 61511 clauses 11 and 12 |  |  |

| - Factory Acceptance Tests (FATs) |  | status |
| --- | --- | --- |
| Responsible | Instrumentation engineer |  |
| Objective | To verify if systems / cabinets are realised correctly |  |
| Basis | SRS and P&IDs, FAT procedures, Design documents, relevant specification / requisition, vendor documents (e.g. safety manuals), vendor audit report |  |
| Activities | Organise FATs, determine participants, vendor to make test provisions |  |
|  | Perform FATs |  |
|  | Verify the Application Program in the safety PLC |  |
| Deliverables | FAT reports |  |
| Reference: IEC 61511 clause 13 |  |  |

| - Functional Safety Assessment stage 2 (FSA 2) |  | status |
| --- | --- | --- |
| Responsible | Competent independent engineer |  |
| Objective | To ensure that the activities of the SIS life-cycle phases ‘Design of the SIS’ and ‘FATs’ have been performed correctly |  |
| Basis | SRS and P&IDs, Design documents, FAT reports, specifications / requisitions and vendor documents |  |
| Activities | Verification if involved personnel are competent |  |
|  | Verification if the recommendations of FSA-1 are implemented |  |
|  | Verification of design documents |  |
|  | Verification of the Application Program documents |  |
|  | Verification if the FAT recommendations are implemented |  |
| Deliverable | FSA 2 report |  |
| Reference: IEC 61511 clause 5.2.6.1 |  |  |

| - SIS installation and commissioning |  | status |
| --- | --- | --- |
| Responsible | Instrumentation engineer |  |
| Objectives | To realise and pre-test the SIS |  |
| Basis | Installation plan, design documents, vendor documents, FAT reports, FSA 2 report, Loop test procedures |  |
| Activities | Installation of the SIS |  |
|  | Commissioning of the SIS so that it is ready for final system validation. |  |
| Deliverables | As built marked-up design documents |  |
|  | Records of the commissioning of the SIS |  |
| Reference: IEC 61511 clause 14 |  |  |

| - SIS safety validation |  | status |
| --- | --- | --- |
| Responsible | Instrumentation engineer |  |
| Objective | To validate that the installed and commissioned SIS and its associated SIFs achieve the requirements as stated in the SRS |  |
| Basis | SRS’s, proof test procedures, validation procedures, design documents, vendor documents, FAT reports |  |
| Activities | Perform inspections and tests |  |
| Deliverables | Validation report |  |
|  | Update of the SIS maintenance management database with the test results |  |
| Reference: IEC 61511 clause 15 |  |  |

| - Functional Safety Assessment 3 (FSA 3) – SIL Field validation |  | status |
| --- | --- | --- |
| Responsible | Competent independent engineer |  |
| Objective | To ensure that the activities of the SIS life-cycle phases ‘SIS installation and Commissioning’ and ‘SIS safety validation’ have been performed correctly |  |
| Basis | P&ID’s, SRS, design documents, vendor documents, validation procedures & validation results, proof test procedures and proof test results |  |
| Activities | Verification if involved personnel are competent |  |
|  | Verification if the proof tests / validations procedures are adequate |  |
|  | Verification if all tests / validations are performed, evaluation of the test results |  |
|  | Visual inspection of SIS instruments |  |
| Deliverable | FSA 3 report |  |
| Reference: IEC 61511 clause 5.2.6.1 |  |  |

| - Operation and maintenance |  | status |
| --- | --- | --- |
| Responsible | Project / Operations / Maintenance managers |  |
| Objective | To maintain the SIL of each SIF, to operate and maintain the SIS in a way that sustains the required safety functions |  |
| Basis | Validated SIS and Up-to-date SIS documents |  |
| Activities | Implement the recommendations of FSA 3 |  |
|  | Take care of awareness and competence of personnel |  |
|  | Organise operators training |  |
|  | Organise maintenance training |  |
|  | Perform periodical proof tests and visual inspections |  |
|  | Keep the maintenance management database up-to-date |  |
|  | Use approved procedures for bypassing elements of the SIF when needed |  |
|  | Perform preventive and breakdown maintenance of the SIS, e.g. periodical overhaul of valves by valve vendor and calibration of sensors |  |
|  | Take care of adequate spare parts and service contracts |  |
| Reference: IEC 61511 clause 16 |  |  |

| Abbreviations |  |
| --- | --- |
| FAT | Factory Acceptance Test |
| FLD | Functional Logic Diagrams |
| FSA | Functional Safety Assessment |
| HAZOP | HAZARD & Operability |
| PFD | Average Probability of Failure on Demand |
| PLC | Programmable Logic Controller |
| P&ID | Piping & Instrumentation Diagram |
| RA | Risk Assessment |
| SIF | Safety Instrumented Function |
| SIL | Safety Integrity Level |
| SIS | Safety Instrumented System |
| SRS | Safety Requirements Specification |
| Reference: IEC 61511 clause 3 |  |