## SRS template
Safety Requirement Specification
SIF identification & references
SIF name/number
Document date
Revision
SIF description
P&ID Reference
H&RA reference
Other References
Hazard & Risk Assessment
Hazardous Event
Safe state of process
Expected demand rate
Process details
Process Safety Time
Assumptions/calculations
Allowable leak rate of valves
Assumptions/calculations
Other requirements
SIF specification
Required SIL
Required Risk Reduction or PFD
Mode of operation
Fouling / plugging / tracing req.
Trip setpoint
Energize / de-energize to trip
Manual shutdown required
Reset SIF after activation
SIS lifetime
Operational (Start-up) overrides
Maintenance bypasses/overrides
Application Program requirements
Operator interface
Summary of Inputs / Outputs
Sensors |  | Tag name | Type | Range
Sensor 1
Sensor 2
Sensor 3
Configuration
Desired proof test interval
Special (proof test) requirements
Desired response to Failure Modes
Logic solver |  | Tag name | Type
LS
Final elements |  | Tag name | Type | Action
Final element 1
Final element 2
Final element 3
Configuration
Desired proof test interval
Special (proof test) requirements
Attachments
Approvals |  | Name | Function | Date
Approved by
Terms of reference
1. The Safety Requirement Specification (SRS) is a multidisciplinary document in which all relevant aspects are specified in order to be able to perform the design and engineering of the SIS.
2. The SRS shall be approved by a multidisciplinary team, for example the Hazard & Risk Assessment team.
3. The SRS shall be used as well as reference document for verification / validation activities.
4. Relevant documents could be attached to the SRS, e.g. cause & effect diagrams, control narratives, trip setting list, (test) procedures.

## SRS template explantion
Safety Requirement Specification
SIF identification & references
SIF name/number |  | Enter the unique name or tag-number of the SIF.
Document date |  | Creation date of SRS.
Revision |  | Revision number
SIF description |  | Describe how the SIF should work, i.e. its function and how it will prevent a dangerous scenario to develop.
P&ID Reference |  | Reference to the P&IDs which are relevant to the SIF.
H&RA reference |  | Reference to PHA document.
Other References |  | Reference to other relevant document.
Hazard & Risk Assessment
Hazardous Event |  | Describe the hazardous event for which the SIF is needed. This can be from a Process Hazard Analysis like HAZOP and LOPA.
Safe state of process |  | Describe the safe state of the process.
Expected demand rate |  | How often will the scenario develop if there are no safeguards present.
Process details
Process Safety Time
Assumptions/Calculations |  | Define the period of time between a failure occurring in the system and the occurrence of the hazardous event if the safety function is not performed.
Allowable leak rate of valves
Assumptions/Calculations |  | Define the maximum flow that can leak by a valve used as the final element in a scenario without exceeding a threshold consequence criteria.
Other requirements |  | Describe other relevant requirements.
SIF specification
Required SIL
Required Risk Reduction or PFD
Mode of operation |  | High/Low Demand or Continuous Mode
Fouling / plugging / tracing req. |  | Describe if issues are expected due to fouling/plugging of the medium. Is tracing of sensor impulse lines needed?
Trip setpoint
Energize / de-energize to trip
Manual shutdown required
Reset SIF after activation
SIS lifetime |  | Lifetime of the SIS.
Operational (Start-up) overrides |  | Describe the required operational overrides which impact the SIF.
Maintenance bypasses/overrides |  | Describe the required maintenance bypasses which impact the SIF.
Application Program requirements |  | Describe how the Application Program should look like. For example by use of logic diagrams or control narratives.
Operator interface |  | Describe the operator interface with the SIS. For example; how should an alarm look like?
Summary of Inputs / Outputs
Sensors |  | Tag name | Type | Range
Sensor 1 |  | Tagnr, I/O name | Type of instrument | Instrument range
Sensor 2
Sensor 3 |  | Add extra lines if required
Configuration |  | Voting, i.e. 1oo2
Desired proof test interval |  | Describe the desired proof test interval, for example with respect to turnaround interval or legal requirements.
Special (proof test) requirements |  | Describe additional requirements needed to perform perfect proof testing. For example special connections to pressurize a pressure transmitter.
Desired response to Failure Modes |  | Describe what should happen if a failure is detected (internal diagnostics) or happens (i.e. utility failure, open / short circuit).
Logic solver |  | Tag name | Type
LS |  | Tagnr, I/O name | i.e. PLC, Relais system
Final elements |  | Tag name | Type | Action
Final element 1 |  | Tagnr, I/O name | i.e. Valve, Pump | i.e. Close, Open, Stop
Final element 2
Final element 3 |  | Add extra lines if required
Configuration |  | Voting, i.e. 1oo2
Desired proof test interval |  | Describe the desired proof test interval, for example with respect to turnaround interval or legal requirements.
Special (proof test) requirements |  | Describe additional requirements needed to perform perfect proof testing. For example special connections to perform leak testing.
Attachments |  | Space for relevant attachments. You can insert documents by clicking Insert --> Object --> Create from file (select 'Display is icon')
Approvals |  | Name | Function | Date
Approved by |  | Person name | Person function | Approval date
Add extra lines if required
Terms of reference
1. The Safety Requirement Specification (SRS) is a multidisciplinary document in which all relevant aspects are specified in order to be able to perform the design and engineering of the SIS.
2. The SRS shall be approved by a multidisciplinary team, for example the Hazard & Risk Assessment team.
3. The SRS shall be used as well as reference document for verification / validation activities.
4. Relevant documents could be attached to the SRS, e.g. cause & effect diagrams, control narratives, trip setting list, (test) procedures.

## Example SRS SIF-100
Safety Requirement Specification
SIF identification & references
SIF name/number |  | SIF-100 - Overfill protection
Document date |  | 2022-01-04
Revision |  | 1
SIF description |  | On high level in reactor R-100, measured with LT-100, LT-200 and LT-300 the feed supply should be stopped by closing V-100 and V-200 and stop pump P-100.
P&ID Reference |  | PID-100, rev. A (03/01/2022)
H&RA reference |  | HAZOP Reactor R-100, rev. A (09/07/2021)
Other References |  | LOPA scenario R-100, rev. B (15/10/2021)
Hazard & Risk Assessment
Hazardous Event |  | Feed supply control loop (CV-100 with FT-100) fails open during filling of the reactor. Reactor will overfill via overfill line, causing potential health issues to personnel.
Safe state of process |  | Level below 90% in the reactor.
Expected demand rate |  | Less than once every 10 years
Process details
Process Safety Time |  | 6 minutes
Assumptions/Calculations |  | At setpoint of 95%, the free space is 2m3. Normal feed flow is 20 m3/h. This gives 6 minutes of time before the reactor will overfill. (2m3 / 20m3/h = 6 minutes)
Allowable leak rate of valves |  | 1,3 litre / hour
Assumptions/Calculations |  | At setpoint of 95%, the free space is 2m3. It is assumed that operations will act within 24 hours after 95% is reached. 2m3/24h = 83L/h = 1,3 L/min
Other requirements |  | Valve should close in >8 seconds in order to prevent water hammer.
SIF specification
Required SIL |  | SIL 2
Required Risk Reduction or PFD |  | 200
Mode of operation |  | Low demand
Fouling / plugging / tracing req. |  | Clean medium, no fouling or plugging expected. Impulse lines should be traced due to winterization.
Trip setpoint |  | 95%
Energize / de-energize to trip |  | De-energize to trip
Manual shutdown required |  | Yes
Reset SIF after activation |  | Yes
SIS lifetime |  | 20 years
Operational (Start-up) overrides |  | Override SIS during cleaning
Maintenance bypasses/overrides |  | Sensors should be able to be bypassed during maintenance, e.g. sensor calibration.
Application Program requirements |  | See functional logics diagram in attached document SIF-100 AP requirements.
Operator interface |  | On SIS activation, the alarm should be visible and audible on Alarm Panel AP-10 and via DCS.
Summary of Inputs / Outputs
Sensors |  | Tag name | Type | Range
Sensor 1 |  | LT-100 | Level transmitter (guided wave radar) | 0-100% (0-4m)
Sensor 2 |  | LT-200 | Level transmitter (guided wave radar) | 0-100% (0-4m)
Sensor 3 |  | LT-300 | Level transmitter (dP measurement) | 0-100% (0-4m)
Configuration |  | 2oo3
Desired proof test interval |  | 4 years (due to turnaround schedule).
Special (proof test) requirements |  | Equip pressure sensing line of LT-300 with interlocking devices to enable pressure tests / calibration.
Desired response to Failure Modes |  | Upon failure of the sensors the signal shall fail to the upscale direction (high; >20mA). The DCS should exclude this sensor from the voting and give an alarm. Trip if alarm is active for 8 hours.
Logic solver |  | Tag name | Type
LS |  | LS-100 | Safety PLC (SIL-3)
Final elements |  | Tag name | Type | Action
Final element 1 |  | V-100 | ESD Valve (Air-to-Open) | Close
Final element 2 |  | V-200 | ESD Valve (Air-to-Open) | Close
Final element 3 |  | P-100 | Pump (driven by VSD) | Stop
Configuration |  | 1oo2
Desired proof test interval |  | 4 years (due to turnaround schedule).
Special (proof test) requirements |  | V-100 and V-200 should close slowly (>30 seconds) in order to prevent water hammering. Inline leak testing of V-100 and V-200 should be possible.
Attachments
Approvals |  | Name | Function | Date
Approved by |  | Person A | Operator | 2022-01-05
|  | Person B | Process Engineer | 2022-01-05
|  | Person C | Instrumentation & Control Engineer | 2022-01-05
|  | Person D | Maintenance Engineer | 2022-01-05
|  | Person E | Process Safety Engineer | 2022-01-05
Terms of reference
1. The Safety Requirement Specification (SRS) is a multidisciplinary document in which all relevant aspects are specified in order to be able to perform the design and engineering of the SIS.
2. The SRS shall be approved by a multidisciplinary team, for example the Hazard & Risk Assessment team.
3. The SRS shall be used as well as reference document for verification / validation activities.
4. Relevant documents could be attached to the SRS, e.g. cause & effect diagrams, control narratives, trip setting list, (test) procedures.

## Revision
SRS template revision data
Date | Version | Description | Author
2018-12-20 | 1.0 | Initial version | Jeroen Mijnarends
2022-01-05 | 2.0 | Mode of operation and SIS lifetime added. | Jeroen Mijnarends